## English
| MEASURING POINT |  | _HAD10CL901/CL001/CL002/CL003 | [8 empty] | REFERENCES FOR APPLICATIONS, OBSERVATIONS (ABREVIATIONS)
| FUNCTIONAL CODE |  | HAD10 | [8 empty] | W | WARNING | YP12
| FUNCTIONAL GROUP |  | H1 | [6 empty] | LIMIT-/ | SIGNAL | SP | SETPOINT
| RANGE |  | mm |  | .... |  |  |  |  | SETPOINT- | OUTPUT | A | ALARM | YP11
| REDUNDANCY |  | 2 of 3 | [6 empty] | SETTING | (TEXT) | Z | PROTECTION
|  |  |  | Signal code |  | Signal activated |  |  | mm | mm |  | T | TOLERANCE | YP13 |  |  |  |  | processing by
|  |  |  | CL901 | CL001/2/3 | Normal Operation | Start-up | Shutdown | from centerline | from bottom
| HAD10 |  |  |  | XH07 | X | X | X | 230 | 1144.5 | >MAX4 | Z, A | Prot close: FW S/O-V LAB30AA001/FW B/P S/O-V LAB30AA011 and FW PMP trip by non-equivalence
| BB001 |  |  | XH05 |  | X | X | X | 180 | 1094.5 | >MAX3 | W | Prot open: I-B/D C-V HAD20AA101 and S/O-V HAD20AA001
|  |  |  | XH03 |  | X | X | X | 130 | 1044.5 | >MAX2 | SP4, W | SP for opening of I-B/D C-V HAD20AA101, Prot. Close of FW C-V LAB30AA101 and FW B/P C-V LAB30AA102
|  |  |  | XH01 |  | X | - | X | 85 | 999.5 | >MAX1 | T | Control range exceeded
[9 empty] | 0 | 914.5 | CL | SP3 | Operating level
| TANK |  |  | XH52 |  | X | - | - | 114.5 | 800 | <MIN1 | T | Control range exceeded
| DESIGNATION |  |  | XH04 |  | - | X | - | 214.5 | 700 | >MIN2 |  | Water ejection; first steam; C/O to OP LVL;
| HP-DRUM |  |  | XH54 |  | X | - | - | 214.5 | 700 | <MIN2 | W | HRSG S/D if FW S/O-V LAB30AA001 closed
|  |  |  | XH56 |  | - | X | X | 545 | 369.5 | <MIN3 | SP1+40mm
|  |  |  | XH58 |  | - | X | X | 585 | 329.5 | <MIN4 | SP1 | HRSG start-up filling setpoint; C/O to LVL CTRL
|  |  |  | XH10 |  | - | X | X | 625 | 289.5 | >MIN5 | SP1-40mm
|  |  |  | XH60 |  | X | X | X | 625 | 289.5 | <MIN5 | W | Prot close: B/D valves HAD20AA101/001 and HAD15AA001
[5 empty] | ZH62 | X | X | X | 790 | 124.5 | <MIN6 | Z, A
[10 empty] | 0 |  |  | Tank Bottom (Internal)
| INDICATION |  | (I) | X | [5 empty] | TANK DATA
| RECORDING |  | (R) | X | [5 empty] | POSITION HORIZONTAL/VERTICAL |  |  |  |  | HORIZONTAL | WITH/ | WITHOUT EQUALIZING CHAMBER
| PROCESS-COMPUTER |  | (Y) | X | [5 empty] | NET CAPACITY |  |  |  | m3 | 15 | WITH/ | WITHOUT SUPERV.OF WATER REF.COLUMN
| CONTROLLING |  | (C) | X | [5 empty] | MEDIUM: |  |  |  |  | feedwater/demineralized water | WITH/ | WITHOUT WATER ADDITION
| SAFETY ACT.(PROTECT.) |  | (Z) | X | [5 empty] | DIAMETER / WALL THICKNESS |  |  |  | mm / mm | 1829 / 92 | CLASSIFICATION
| SWITCHING |  | (S) | X | [5 empty] | OPERATING TEMP. (NORM.): |  |  |  | °C | 329 | ALLOW.OPER.TEMP. |  |  | (MAX./MIN.)°C | 339 / 20
| ALARM |  | (A) | X | [5 empty] | OPERATING PRESSURE (NORM.): |  |  |  | bar abs. | 127 | ALLOW.OPER.PRESS. |  |  | (MAX./MIN.) bar abs. | 144 / 1
[10 empty] | DENSITY |  |  |  | kg/m3 | 643 | PRESSURE TEST |  |  | bar | 214.5
| Dept: | W713 |  | MF-Ident-No.:
c | Revision | 2002-11-22 | Weselmann | Date | 2002-03-11 |  | Campo de Gibraltar SPA224 | [6 empty] | HAD10 |  |  |  | XW02 | HAD10BB001
b | Revision | 2002-07-16 | Weselmann | Drawn | Weselmann | [8 empty] | HP-Drum
a | First Issue | 2002-03-11 | Weselmann | Appr. | M.Christensen |  | Module Library |  |  |  | ZDX029 ZB | Power Generation | [7 empty] | Sheet 1/1
Rev. | Remarks | Date | Name | Norm |  |  | Orig./Repl. for/Repl. by | [6 empty] | Vessel Protection Sheet
s
The reproduction, transmission or use of this document or its contents is not permitted without express written outhority. Offenders will be liable for damages. All rights, including rights created by patent grant or registration of a utility model or design, are reserved.
The reproduction, transmission or use of this document or its contents is not permitted without express written outhority. Offenders will be liable for damages. All rights, including rights created by patent grant or registration of a utility model or design, are reserved.

## Spanish
| PUNTO DE MEDICIÓN |  | _HAD10CL901/CL001/CL002/CL003 | [8 empty] | REFERENCIAS PARA APLICACIONES, OBSERVACIONES (ABREVIATURAS)
| CÓDIGO FUNCIONAL |  | HAD10 | [8 empty] | W | ADVERTENCIA | YP12
| GRUPO FUNCIONAL |  | H1 | [6 empty] | LÍMITE-/ | SEÑAL | SP | PUNTO DE AJUSTE
| RANGO |  | mm |  | .... |  |  |  |  | PTO.AJ.- | SALIDA | A | ALARMA | YP11
| REDUNDANCIA |  | 2 de 3 | [6 empty] | PARÁMETRO | (TEXTO) | Z | PROTECCIÓN
|  |  |  | Cód. de Salida |  | Señal activada |  |  | mm | mm |  | T | TOLERANCIA | YP13 |  |  |  |  | Procesamiento por
|  |  |  | CL901 | CL001/2/3 | Oper. Normal | Arranque | Paro | desde línea central | desde abajo
| HAD10 |  |  |  | XH07 | X | X | X | 230 | 1144.5 | >MAX4 | Z, A | Cierre por Prot: FW S/O-V LAB30AA001/FW B/P S/O-V LAB30AA011 y FW PMP disparado por no-equivalencia
| BB001 |  |  | XH05 |  | X | X | X | 180 | 1094.5 | >MAX3 | W | Cierre por Prot: I-B/D C-V HAD20AA101 y S/O-V HAD20AA001
|  |  |  | XH03 |  | X | X | X | 130 | 1044.5 | >MAX2 | SP4, W | SP para apertura de I-B/D C-V HAD20AA101, Cierre por Prot de FW C-V LAB30AA101 y FW B/P C-V LAB30AA102
|  |  |  | XH01 |  | X | - | X | 85 | 999.5 | >MAX1 | T | Rango de Control excedido
[9 empty] | 0 | 914.5 | CL | SP3 | Nivel de Operación
| TANQUE |  |  | XH52 |  | X | - | - | 114.5 | 800 | <MIN1 | T | Rango de Control excedido
| DESIGNACIÓN |  |  | XH04 |  | - | X | - | 214.5 | 700 | >MIN2 |  | Eyección de Agua; primer vapor; C/O a OP LVL;
| CALDERÍN HP |  |  | XH54 |  | X | - | - | 214.5 | 700 | <MIN2 | W | HRSG S/D si FW S/O-V LAB30AA001 está cerrado
|  |  |  | XH56 |  | - | X | X | 545 | 369.5 | <MIN3 | SP1+40mm
|  |  |  | XH58 |  | - | X | X | 585 | 329.5 | <MIN4 | SP1 | HRSG punto de ajuste de relleno para arranque; C/O to LVL CTRL
|  |  |  | XH10 |  | - | X | X | 625 | 289.5 | >MIN5 | SP1-40mm
|  |  |  | XH60 |  | X | X | X | 625 | 289.5 | <MIN5 | W | Cierre para Prot: válvulas B/D HAD20AA101/001 y HAD15AA001
[5 empty] | ZH62 | X | X | X | 790 | 124.5 | <MIN6 | Z, A
[10 empty] | 0 |  |  | Fondo del Tanque (Interna)
| INDICACIÓN |  | (I) | X | [5 empty] | DATOS DEL TANQUE
| REGISTRANDO |  | (R) | X | [5 empty] | POSICIÓN HORIZONTAL/VERTICAL |  |  |  |  | HORIZONTAL | CON/ | SIN CÁMARA DE IGUALACIÓN
| COMPUTADORA DE PROCESO |  | (Y) | X | [5 empty] | CAPACIDAD NETA |  |  |  | m3 | 15 | CON/ | SIN SUPERV. DE COLUMNA DE AGUA DE REF.
| CONTROLANDO |  | (C) | X | [5 empty] | MEDIO: |  |  |  |  | agua de alimentación/agua desmineralizada | CON/ | SIN ADICIÓN DE AGUA
| ACT. DE SEGURIDAD.(PROTECC.) |  | (Z) | X | [5 empty] | DIÁMETRO / ESPESOR DE PARED |  |  |  | mm / mm | 1829 / 92 | CLASIFICACIÓN
| CONMUTAR |  | (S) | X | [5 empty] | TEMP. DE TRABAJO. (NORM.): |  |  |  | °C | 329 | TEMP. DE TRAB. PERMISIBLE |  |  | (MAX./MIN.)°C | 339 / 20
| ALARMA |  | (A) | X | [5 empty] | PRESIÓN DE TRABAJO (NORM.): |  |  |  | bar abs. | 127 | PRESIÓN DE TRABAJO PERMISIBLE |  |  | (MAX./MIN.) bar abs. | 144 / 1
[10 empty] | DENSIDAD |  |  |  | kg/m3 | 643 | PRUEBA DE PRESIÓN |  |  | bar | 214.5
| Depto.: | W713 |  | Num.-Ident-MF:
c | Revisión | 2002-11-22 | Weselmann | Fecha | 2002-03-11 |  | Campo de Gibraltar SPA224 | [6 empty] | HAD10 |  |  |  | XW02 | HAD10BB001
b | Revisión | 2002-07-16 | Weselmann | Dibujó | Weselmann | [8 empty] | Calderín HP
a | Primera Emisión | 2002-03-11 | Weselmann | Aprobó | M.Christensen |  | Librería de Módulos |  |  |  | ZDX029 ZB | Generación de Potencia | [7 empty] | Hoja 1/1
Rev. | Comentarios | Fecha | Nombre | Norma |  |  | Orig./Respond. para/Respond. por | [6 empty] | Hoja de Protección del Contenedor
s
La reproducción, transmisión, o uso de este documento o sus contenidos no están permitidos sin autorización escrita expresamente. Los infractores serán responsables por los daños. Todos los derechos reservados, inclouyendo los derechos creados por la conseción de patente o registro de un modelo o diseño utilitario.